**Maintenance -Test & Tag Inspection Intervals Electrical Equipment**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **Type of environment and/or equipment** | **Interval between inspection and tests** | | | | |
| **Equipment including Class I (protectively earthed), Class II (double insulated), cord sets, cord extension sets and power boards** | **Residual Current Devices (Safety Switches)** | | | |
| **Push button test by user** | | **Operating time and push button test by licensed tester** | |
| **Portable** | **Fixed** | **Portable** | **Fixed** |
| Environment where equipment or flexible cord is subject to flexing in normal use OR is open to abuse OR is in a hostile environment | 12 months | 3 months | 6 months | 12 months | 12 months |
| Environment where the equipment or supply flexible cord is NOT subject to flexing in normal use OR is open to abuse OR is NOT in a hostile environment | 5 years | 3 months | 6 months | 2 years | 2 years |

* Hostile environment examples include use in a workshop, vibration, dirty or dusty, wet, hot surfaces or cables near heat sources, risk of chemical damage
* Source AS3760:2010